# SOP-PM-440: Gas Turbine T-800 Inspection Procedure

Standard Operating Procedure for preventative maintenance and hot-section borescope inspection.

# 1. Safety Prerequisites

Lockout/Tagout (LOTO) procedure #LOTO-GT-08 must be executed prior to unlatching enclosure access doors.

Allow turbine casing temperature to fall below 50 deg C before inserting optical borescope guide tubes.

# 2. Inspection Criteria Table

| Component | Acceptable Limit | Action Threshold |
| --- | --- | --- |
| Stage 1 Nozzle Guide Vanes | Thermal oxidation < 0.2 mm depth | Cracks exceeding 1.5 mm require blade set replacement |
| Combustor Liner Transition Piece | Minor surface crazing allowable | Perforations or buckling require immediate overhaul |
| Power Turbine Rotor Shrouds | Rub depth <= 0.35 mm | Blade tip clearance deficit under 0.8 mm |

# 3. Handover and Restart Authorizations

Inspection results must be logged into the local Edge intelligence database. Lead maintenance technician signoff required.